## Slide 1
Sub Distribution Board (SDB) & Emergency Sub Distribution Board (ESDB)
Prepared by,
Raisa Bentay Hossain (1606151)
Partho Ghosh (1606161)

## Slide 2
Ground Floor

## Slide 3
Ampere Rating, I=
CKT1 Rating | SB 1 | 0.7 A | 2 x 1.5 rm BYM + 1.5 BYA ECC are used
CKT2 Rating | SB 2,3 | 2.69 A | 
CKT3 Rating | SB 4,5 | 0.76 A | 
CKT4 Rating | SB 6 | 0.84 A | 
CKT5 Rating | SB 7,8 | 2.75 A | 
pf = 0.75 & V = 220 V
CKT No | Switch Board Under The CKT | Ampere Rating Calculated | Wire Used
Ground Floor

## Slide 4
Ground Floor

## Slide 5
1st and 2nd Floor

## Slide 6
1st and 2nd Floor

## Slide 7
Ampere Rating, I=
CKT1 Rating | SB 1,2,6 | 4.81 A | 2 x 1.5 rm BYM + 1.5 BYA ECC
CKT2 Rating | SB 4,5,8 | 5.11 A | 2 x 2.5 rm BYM + 2.5 BYA ECC
CKT3 Rating | SB 3 | 1.88 A | 2 x 1.5 rm BYM + 1.5 BYA ECC
CKT4 Rating | SB 7,9,10 | 4.73 A | 
CKT5 Rating | SB 11 | 0.28 A | 
pf = 0.75 & V = 220 V
CKT No | Switch Board Under The CKT | Ampere Rating Calculated | Wire Used
1st and 2nd Floor

## Slide 8
1st and 2nd Floor

## Slide 9
SDB load= Total load x 0.7 + Total P socket load x 0.2 + Total Q socket x 0.2
Total Load = CKT1 load + CKT2 load + CKT3 load + CKT4 load + CKT5 load
SDB Current =
P Load = 2500 W
Q Load = 4000W
Voltage = 220 V
Power Factor, pf = 0.75
Calculations for SDB

## Slide 10
Name | Load | Total Load | SDB Load | SDB Current | Decision
CKT1 Load | 115W | 1320W | (1320W * 0.7) + (2500W * 0.2) = 1424W |  | 10 A SP MCCB is needed from SDB to MDB
CKT2 Load | 488W |  |  |  | 
CKT3 Load | 126 |  |  |  | 
CKT4 Load | 138W |  |  |  | 
CKT5 Load | 453W |  |  |  | 
P Socket Load | 1* 2500W | 2500 W |  |  | 
Q socket Load | 0* 4000W | 0 W |  |  | 
Name | Load | Total Load | SDB Load | SDB Current | Decision
CKT1 Load | 115W | 1320W | (1320W * 0.7) + (2500W * 0.2) = 1424W |  | 10 A SP MCCB is needed from SDB to MDB
CKT2 Load | 488W |  |  |  | 
CKT3 Load | 126 |  |  |  | 
CKT4 Load | 138W |  |  |  | 
CKT5 Load | 453W |  |  |  | 
P Socket Load | 1* 2500W | 2500 W |  |  | 
Q socket Load | 0* 4000W | 0 W |  |  | 
SDB for Ground Floor

## Slide 12
Name | Load | Total Load | SDB Load | SDB Current | Decision
CKT1 Load | 793W | 2772W | (2772W * 0.7) + (6 * 2500W * 0.2) + (3 * 4000W * 0.2) = 7340.4 W |  | 50 A SP MCCB is needed from SDB to MDB
CKT2 Load | 843W |  |  |  | 
CKT3 Load | 310W |  |  |  | 
CKT4 Load | 780W |  |  |  | 
CKT5 Load | 46W |  |  |  | 
P Socket Load | 6* 2500W | 15000 W |  |  | 
Q socket Load | 3* 4000W | 12000 W |  |  | 
Name | Load | Total Load | SDB Load | SDB Current | Decision
CKT1 Load | 793W | 2772W | (2772W * 0.7) + (6 * 2500W * 0.2) + (3 * 4000W * 0.2) = 7340.4 W |  | 50 A SP MCCB is needed from SDB to MDB
CKT2 Load | 843W |  |  |  | 
CKT3 Load | 310W |  |  |  | 
CKT4 Load | 780W |  |  |  | 
CKT5 Load | 46W |  |  |  | 
P Socket Load | 6* 2500W | 15000 W |  |  | 
Q socket Load | 3* 4000W | 12000 W |  |  | 
SDB for 1st & 2nd Floor

## Slide 13
1st and 2nd Floor

## Slide 14
Emergency Sub Distribution Board (ESDB)

## Slide 15
CKT1’ Rating | 0.36 A | 2 x 1.5 rm BYM + 1.5 BYA ECC are used
CKT2’ Rating | 0.36 A | 
CKT3’ Rating | 0.139 A | 
CKT4’ Rating | 0.139 A | 
CKT5’ Rating | 0.36 A | 
CKT No | Ampere Rating Calculated | Wire Used
Ground Floor

## Slide 17
CKT1’ Rating | 1.68 A | 2 x 1.5 rm BYM + 1.5 BYA ECC are used
CKT2’ Rating | 0.24 A | 
CKT3’ Rating | 0.745 A | 
CKT4’ Rating | 0.7 A | 
CKT5’ Rating | 0.424 A | 
CKT6’ Rating | 0.14 A | 
CKT No | Ampere Rating Calculated | Wire Used
1st and 2nd Floor

## Slide 18
1st and 2nd Floor

## Slide 19
Calculations for ESDB
Floor | Total Load | P and Q socket load | ESDB load | ESDB Current | Decision
Ground Floor | 226W | 2500W | 658.2W |  | 5 A SP MCCB
1st and 2nd Floor | 649W | 3 * 2500W + 1*4000W | 2754.3 W |  | 20 A SP MCCB
Floor | Total Load | P and Q socket load | ESDB load | ESDB Current | Decision
Ground Floor | 226W | 2500W | 658.2W |  | 5 A SP MCCB
1st and 2nd Floor | 649W | 3 * 2500W + 1*4000W | 2754.3 W |  | 20 A SP MCCB

## Slide 21
1st and 2nd Floor